Hand-Calculation Package

Two-stage magnetic-bearing centrifugal compressor (Turbocor TTS350 class, R-513A)

Free-body diagrams, control volumes and every sizing calculation behind the design

How to use this package: each calculation follows the same pattern used in engineering calc books: Given, Find, Assumptions, Equations, Solution, Result. Values come from the design scripts in this repository (meanline.py and hand_calcs.py), so every number can be reproduced with a calculator and a refrigerant property table. Properties are real-gas R-513A from CoolProp (a 56/44 % by mass R-1234yf/R-134a mixture), except calculation C19, which uses R-134a to match the CFD material.

Calculations C14–C18 (bearing loads, unbalance, axial thrust, disc stress, critical speed) are first-order estimates made for this package. They use simplified models and are labelled as such. Use them to check orders of magnitude, not as final design values.

# Contents

Right-click and choose Update Field in Word to fill in the page numbers.

# C1  Design requirements and refrigerant state points

FBD-1. Chiller cycle with the four state points and the compressor control volume.

GIVEN

- Capacity Q̇_evap = 110 tons × 3.51685 kW/ton = 386.9 kW (TCAA220, two compressors)

- Saturated suction 3.5 °C, saturated discharge 51.5 °C (AHRI air-cooled rating)

- Superheat 3 K at compressor inlet, subcooling 5 K leaving the condenser

- Refrigerant R-513A

FIND

- Evaporator and condenser pressures, inlet state (1), liquid enthalpy (3 = 4)

ASSUMPTIONS

- Steady state; no pressure drop in heat exchangers or piping

- Throttling at the expansion valve is isenthalpic (h₄ = h₃)

EQUATIONS

P_evap = P_sat(T_evap),   P_cond = P_sat(T_cond)

State 1: (P_evap, T_evap + 3 K) → h₁, s₁, ρ₁, a₁

State 3: (P_cond, T_cond − 5 K) → h₃ = h₄

SOLUTION

P_evap = P_sat(3.5 °C) = 364.3 kPa

P_cond = P_sat(51.5 °C) = 1,420.1 kPa

State 1: T₁ = 6.5 °C → h₁ = 383.57 kJ/kg, s₁ = 1.7126 kJ/kg·K, ρ₁ = 18.92 kg/m³, a₁ = 141.1 m/s

State 3: T₃ = 46.5 °C → h₃ = h₄ = 267.86 kJ/kg

Result: P_evap = 364 kPa, P_cond = 1,420 kPa, h₁ = 383.6 kJ/kg, h₄ = 267.9 kJ/kg

# C2  Mass flow and suction volume flow

GIVEN

- Q̇_evap = 386.9 kW, h₁ = 383.57 kJ/kg, h₄ = 267.86 kJ/kg, ρ₁ = 18.92 kg/m³

FIND

- Refrigerant mass flow ṁ and suction volume flow V̇

ASSUMPTIONS

- Evaporator control volume: steady, no work, negligible kinetic/potential energy changes

EQUATIONS

Q̇_evap = ṁ (h₁ − h₄)

V̇ = ṁ / ρ₁

SOLUTION

q_evap = h₁ − h₄ = 383.57 − 267.86 = 115.71 kJ/kg

ṁ = 386.9 / 115.71 = 3.343 kg/s

V̇ = 3.343 / 18.92 = 0.1767 m³/s

Result: ṁ = 3.343 kg/s, V̇ = 0.177 m³/s

# C3  Pressure ratio, ideal work and stage split

FBD-2. Compressor control volume for the steady-flow energy equation.

GIVEN

- P_evap = 364.3 kPa, P_cond = 1,420.1 kPa, s₁ = 1.7126 kJ/kg·K

FIND

- Overall and per-stage pressure ratio; isentropic work

ASSUMPTIONS

- Two stages with equal pressure ratio (first guess); adiabatic compressor

EQUATIONS

PR = P_cond / P_evap,   PR_stage ≈ √PR

Δh₀s = h(P_cond, s₁) − h₁

Ẇ = ṁ (h₀₂ − h₀₁)

SOLUTION

PR = 1,420.1 / 364.3 = 3.899

PR_stage ≈ √3.899 = 1.974

h₂s = h(1,420 kPa, s₁) = 409.74 kJ/kg → Δh₀s = 26.17 kJ/kg

With η_stage = 0.8, stage-1 work ≈ Δh₀s,1/η = 13.23 / 0.8 = 16.53 kJ/kg (iterated: 16.53 kJ/kg)

Result: PR = 3.90 overall, ≈ 1.97 per stage; Δh₀s,total = 26.2 kJ/kg

# C4  Slip factor and work coefficient

FBD-3. Impeller control volume for angular momentum (Euler equation).

GIVEN

- Z = 14 blades (7 main + 7 splitter), exit blade angle β₂b = 40° (backswept, from radial), φ₂ = Cm₂/U₂ = 0.28

FIND

- Slip factor σ and work coefficient ψ = Δh₀/U₂²

ASSUMPTIONS

- No inlet swirl (IGVs open): Cθ₁ = 0

- Wiesner slip correlation; splitters counted as full blades

EQUATIONS

σ = 1 − √(cos β₂b) / Z^0.7   (Wiesner)

Cθ₂ = σ U₂ − Cm₂ tan β₂b

Δh₀ = U₂ Cθ₂ → ψ = σ − φ₂ tan β₂b

SOLUTION

σ = 1 − √(cos 40°) / 14^0.7 = 1 − 0.8752 / 6.343 = 0.862

(for comparison, 7 blades only: σ = 0.776)

ψ = 0.862 − 0.28 × tan 40° = 0.862 − 0.235 = 0.627

Result: σ = 0.862, ψ = 0.627

# C5  Stage-1 tip speed and tip diameter

GIVEN

- Required Δh₀ = 16.53 kJ/kg (from C3, iterated), ψ = 0.627, N = 30,000 rpm

FIND

- Tip speed U₂ and diameter D₂

ASSUMPTIONS

- Both stages use the same D₂ (one shaft, one speed); D₂ iterated until two stages reach P_cond

EQUATIONS

U₂ = √(Δh₀ / ψ)

D₂ = 60 U₂ / (π N)

ω = 2πN/60

SOLUTION

U₂ = √(16,533 / 0.627) = 162.4 m/s

ω = 2π × 30000 / 60 = 3,141.6 rad/s

D₂ = 60 × 162.4 / (π × 30000) = 0.1034 m

Result: U₂ = 162.4 m/s, D₂ = 103.4 mm (r₂ = 51.69 mm)

Note: Check: the tip Mach number U₂/a₁ ≈ 1.15 is typical for refrigerant compressors because refrigerants have low speeds of sound.

# C6  Inlet eye sizing

FBD-4. Velocity triangles at the stage-1 inlet tip and exit, to scale.

GIVEN

- ṁ = 3.343 kg/s, hub/tip ratio D₁h/D₁t = 0.4, ω = 3,141.6 rad/s, inlet total state from C1

FIND

- Eye tip diameter D₁t that minimises the relative Mach number at the blade tip

ASSUMPTIONS

- Uniform axial inflow, no swirl; static density from isentropic acceleration (iterated)

EQUATIONS

A₁ = π/4 (D₁t² − D₁h²),   Cm₁ = ṁ / (ρ₁ A₁)

U₁t = ω D₁t / 2,   W₁t = √(Cm₁² + U₁t²)

M₁rel = W₁t / a₁,   β₁t = atan(U₁t / Cm₁)

SOLUTION

Small D₁t → high Cm₁; large D₁t → high U₁t. Scanning D₁t gives a minimum W₁t at:

D₁t = 67.0 mm, D₁h = 26.8 mm → A₁ = 2,962 mm²

ρ₁,static = 16.92 kg/m³ → Cm₁ = 66.7 m/s

U₁t = 3,141.6 × 0.0335 = 105.2 m/s

W₁t = √(66.7² + 105.2²) = 124.6 m/s → M₁rel = 0.882,  β₁t = 57.6°

Result: D₁t = 67.0 mm, M₁rel = 0.88 (below 0.9, so no strong shock), blade inlet angle β₁t = 57.6° + 2° incidence

# C7  Impeller exit width and exit velocities

GIVEN

- U₂ = 162.4 m/s, φ₂ = 0.28, σ = 0.862, β₂b = 40°, exit static density ρ₂ = 29.17 kg/m³, blockage B = 0.06

FIND

- Exit width b₂, exit velocities, absolute flow angle α₂ and Mach number

ASSUMPTIONS

- Impeller total-to-total efficiency 0.90 to fix the exit state

EQUATIONS

Cm₂ = φ₂ U₂,   Cθ₂ = σU₂ − Cm₂ tan β₂b,   C₂ = √(Cm₂² + Cθ₂²)

b₂ = ṁ / [ρ₂ π D₂ Cm₂ (1 − B)]

α₂ = atan(Cθ₂ / Cm₂)

SOLUTION

Cm₂ = 0.28 × 162.4 = 45.47 m/s

Cθ₂ = 0.862 × 162.4 − 45.47 × tan 40° = 101.82 m/s

C₂ = 111.5 m/s,  α₂ = 65.9°,  M₂ = 0.795

b₂ = 3.343 / (29.17 × π × 0.1034 × 45.47 × 0.94) = 0.00826 m

Result: b₂ = 8.26 mm, Cθ₂ = 101.8 m/s, α₂ = 65.9°, stage-1 PR = 1.979

# C8  Stage 2 (same method as C4–C7)

| Quantity | Stage 1 | Stage 2 |
| --- | --- | --- |
| Inlet total pressure / temperature | 364 kPa / 6.5 °C | 721 kPa / 31.8 °C |
| Tip diameter / tip speed | 103.4 mm / 162.4 m/s | 103.4 mm / 162.4 m/s |
| Eye tip / hub diameter | 67.0 / 26.8 mm | 54.0 / 25.9 mm |
| Cm₁ / W₁t / M₁rel | 66.7 / 124.6 / 0.88 | 56.4 / 101.9 / 0.73 |
| Exit width b₂ | 8.26 mm | 4.21 mm |
| Exit density ρ₂ | 29.2 kg/m³ | 57.3 kg/m³ |
| Work Δh₀ | 16.53 kJ/kg | 16.53 kJ/kg |
| Stage pressure ratio | 1.979 | 1.970 |
| Outlet total pressure / temperature | 721 kPa / 31.8 °C | 1,420 kPa / 60.2 °C |

Stage 2 handles the same mass flow at about twice the density, so its eye is smaller and its exit width is about half that of stage 1.

# C9  Vaneless diffuser and de-swirl vane inlet angle

GIVEN

- r₂ = 51.69 mm, r₃ = 80.1 mm (r₃/r₂ = 1.55), b₃ = 7.43 mm, Cθ₂ = 101.8 m/s, Cm₂ = 45.5 m/s

FIND

- Velocities at the diffuser exit; inlet metal angle of the de-swirl (return-channel) vanes

ASSUMPTIONS

- Free vortex in the vaneless space (no wall friction): r Cθ = constant

- Density nearly constant across the diffuser (first estimate)

EQUATIONS

Cθ₃ = Cθ₂ r₂ / r₃

Cm₃ = Cm₂ (r₂ b₂) / (r₃ b₃)   (continuity)

α₃ = atan(Cθ₃ / Cm₃)

SOLUTION

Cθ₃ = 101.8 × 51.7 / 80.1 = 65.7 m/s

Cm₃ = 45.5 × (51.7 × 8.26) / (80.1 × 7.43) = 32.6 m/s

C₃ = 73.3 m/s (down from 111.5 m/s → static pressure recovery)

De-swirl vane inlet angle (with density correction) = 66.6° from radial

Result: C₃ ≈ 73 m/s; de-swirl vanes: inlet 66.6°, exit 0° (radial, no swirl into stage 2)

# C10  Volute cross-sections

GIVEN

- Volume flow at the volute Q = 45.9 L/s, stage-2 exit angular momentum K = Cθ₂ r₂ = 5.263 m²/s, r₃ = 80.1 mm

FIND

- Circular section diameter d(θ) around the volute

ASSUMPTIONS

- Constant angular momentum (free vortex) inside the volute

- Circular, external sections tangent to the diffuser exit (+2 mm lip)

EQUATIONS

Flow through section θ: Q θ/(2π) = ∫ Cθ dA ≈ K · A / R_c

A(θ) = Q θ R_c / (2π K),   R_c = r₃ + d/2 + 2 mm,   d = √(4A/π)  (iterate)

SOLUTION

| θ (deg) | d (mm) | R_c (mm) | Area (mm²) |
| --- | --- | --- | --- |
| 0 | 0.0 | 82.1 | 0 |
| 45 | 11.0 | 87.6 | 95 |
| 90 | 15.8 | 90.0 | 196 |
| 135 | 19.6 | 91.9 | 300 |
| 180 | 22.8 | 93.5 | 407 |
| 225 | 25.7 | 94.9 | 517 |
| 270 | 28.3 | 96.3 | 629 |
| 315 | 30.8 | 97.5 | 743 |
| 360 | 33.1 | 98.7 | 860 |

Result: d grows from 0 at the tongue to 33.1 mm at 360° (R_c = 98.7 mm)

# C11  Suction and discharge pipe sizing

GIVEN

- V̇_suction = 0.1767 m³/s; discharge density ρ = 72.9 kg/m³ at 1,420 kPa, 60 °C

FIND

- Gas velocity in the DN100 suction and DN50 discharge connections

ASSUMPTIONS

- Target vapour-line velocity about 10–25 m/s (low pressure drop and noise)

EQUATIONS

V = V̇ / (π D² / 4)

SOLUTION

Suction: V = 0.1767 / (π × 0.102² / 4) = 21.6 m/s

Discharge: V̇ = 3.343 / 72.9 = 0.0459 m³/s → V = 21.2 m/s in Ø52.5 mm

Result: Suction DN100: 21.6 m/s; discharge DN50: 21.2 m/s (both within the target range)

# C12  Power, torque, efficiency and kW/ton

GIVEN

- ṁ = 3.343 kg/s, Δh₀ = 16.53 + 16.53 kJ/kg, mechanical loss 2 %, motor × drive efficiency 0.95, ω = 3,141.6 rad/s

FIND

- Gas, shaft and electrical power; torque; overall efficiency; kW/ton and COP

EQUATIONS

Ẇ_gas = ṁ Σ Δh₀,   Ẇ_shaft = Ẇ_gas (1 + 0.02),   Ẇ_in = Ẇ_shaft / 0.95

T = Ẇ_shaft / ω

η_s = Δh₀s / Σ Δh₀,   kW/ton = Ẇ_in / tons,   COP = Q̇_evap / Ẇ_in

SOLUTION

Ẇ_gas = 3.343 × 33.07 = 110.5 kW

Ẇ_shaft = 112.8 kW,  Ẇ_in = 118.7 kW

T = 112,758 / 3,141.6 = 35.89 N·m

η_s = 26.17 / 33.07 = 0.792

kW/ton = 118.7 / 110 = 1.079,  COP = 386.9 / 118.7 = 3.26

Result: Shaft 113 kW, input 119 kW, torque 35.9 N·m, 1.08 kW/ton (compressor only)

# C13  Motor: electrical frequency and rotor shear stress

GIVEN

- N = 30,000 rpm, 2-pole PM motor, T = 35.9 N·m, rotor Ø70 mm × 170 mm active length

FIND

- Inverter output frequency; air-gap shear stress; rotor surface speed

EQUATIONS

f = N p / 120   (p = number of poles)

τ = T / (2π r² L)

v = ω r

SOLUTION

f = 30000 × 2 / 120 = 500 Hz (mains supply is 60 Hz → 3,600 rpm without the drive)

τ = 35.9 / (2π × 0.035² × 0.170) = 27.4 kPa

v = 3,141.6 × 0.035 = 110 m/s

Result: 500 Hz; τ ≈ 27 kPa (typical 20–40 kPa for liquid-cooled high-speed PM motors); 110 m/s surface speed → carbon-fibre retaining sleeve

# C14  Rotor mass, centre of gravity and radial bearing reactions (estimate)

FBD-6. Rotor radial free-body diagram.

GIVEN

- Rotor segment table (drawing TC-103); steel ρ = 7800 kg/m³; aluminium impellers ρ = 2810 kg/m³

- Radial bearing centres x_A = 255 mm, x_B = 520 mm

FIND

- Rotor mass, CG location, static bearing reactions

ASSUMPTIONS

- Shaft segments are solid steel cylinders; impeller mass from a simplified solid of revolution

- Horizontal rotor; gravity only (static)

EQUATIONS

m = Σ mᵢ,   x_CG = Σ mᵢxᵢ / Σ mᵢ

ΣF_y = 0:  R_A + R_B = m g

ΣM_A = 0:  R_B (x_B − x_A) = m g (x_CG − x_A)

SOLUTION

m = 9.52 kg (PM motor section alone ≈ 5.10 kg),  x_CG = 395 mm

W = 9.52 × 9.81 = 93.4 N

R_B = 93.4 × (395 − 255) / 265 = 49.5 N

R_A = 93.4 − 49.5 = 43.9 N

| Segment | Mass (kg) | x (mm) |
| --- | --- | --- |
| impeller nut / nose cone | 0.030 | 90 |
| stage-1 impeller seat | 0.068 | 112 |
| interstage spacer sleeve | 0.081 | 141 |
| stage-2 impeller seat | 0.068 | 169 |
| seal sleeve | 0.119 | 196 |
| front touchdown bearing journal | 0.110 | 215 |
| front radial bearing rotor laminations | 0.919 | 255 |
| shaft | 0.147 | 293 |
| PM motor rotor (magnets + carbon-fibre sleeve) | 5.103 | 385 |
| shaft | 0.196 | 480 |
| rear radial bearing rotor laminations | 0.919 | 520 |
| thrust-disk seat | 0.490 | 575 |
| rear touchdown bearing journal | 0.121 | 611 |
| axial / speed sensor target | 0.025 | 627 |
| thrust disk | 0.784 | 575 |
| impeller 1 | 0.172 | 117 |
| impeller 2 | 0.172 | 174 |

Result: m ≈ 9.5 kg; R_A ≈ 44 N, R_B ≈ 50 N (static)

# C15  Unbalance force at design speed (estimate)

GIVEN

- Rotor mass m = 9.52 kg, ω = 3,141.6 rad/s, balance grade G2.5 (ISO 1940, typical for turbomachinery rotors)

FIND

- Residual unbalance eccentricity and rotating force

EQUATIONS

e = G / ω   (G in m/s)

F = m e ω²

SOLUTION

e = 0.0025 / 3,141.6 = 0.80 μm

F = 9.52 × 0.000000796 × 3,141.6² = 75 N

Result: F_unbalance ≈ 75 N rotating at 1× speed, comparable to the rotor weight, so the magnetic bearings are sized for both

# C16  Axial thrust on the impellers (simplified estimate)

FBD-7. Axial free-body diagram of the two impellers and the thrust disk.

GIVEN

- Static pressures from the meanline: stage 1 eye 324 kPa, exit 572 kPa; stage 2 eye 665 kPa, exit 1,124 kPa

- Face area π(r₂² − r_s²) with r_s = 12 mm → 79.4 cm²

FIND

- Net axial force the axial magnetic bearing must react

ASSUMPTIONS

- Back face sees impeller exit static pressure (no balance holes or seals)

- Open (blade) side sees the average of eye and exit pressure

- Inlet axial momentum ṁCm₁ ≈ ρCm₁²A₁ pushes the impeller toward the motor

EQUATIONS

F_back = p₂ A,   F_front = ½(p_eye + p₂) A,   F_mom = ρ Cm₁² A₁

F_net,i = F_back − F_front − F_mom   (positive = toward suction)

ΣF_x = 0:  F_axial bearing = Σ F_net,i

SOLUTION

Stage 1: 4,538 − 3,557 − 231 = 750 N

Stage 2: 8,927 − 7,104 − 197 = 1,626 N

Result: F_axial ≈ 2.38 kN toward the suction end (upper bound; seals and balance cavities reduce it in practice)

# C17  Impeller disc stress at overspeed (estimate)

FBD-8. Differential element of a rotating disc.

GIVEN

- 7075-T6: ρ = 2810 kg/m³, ν = 0.33, S_y = 503 MPa; r₂ = 51.7 mm, bore r_b = 9 mm

FIND

- Peak hoop stress at 100 %, 115 % (overspeed test) and maximum speed; safety factor

ASSUMPTIONS

- Flat disc of uniform thickness, plane stress; blades ignored (they add load, so FEA is needed to confirm)

EQUATIONS

d(r σ_r)/dr − σ_θ + ρω²r² = 0

σ_θ,max = (3 + ν)/4 · ρω² [r₂² + (1 − ν)/(3 + ν) r_b²]   (at the bore)

SOLUTION

30,000 rpm: σ_θ = 62.1 MPa

34,500 rpm (115 %): σ_θ = 82.1 MPa → SF = 503 / 82.1 = 6.1

39,000 rpm: σ_θ = 104.9 MPa

Result: SF ≈ 6.1 at 115 % overspeed for the disc alone

# C18  First bending critical speed (estimate)

GIVEN

- Steel shaft E = 197 GPa, ρ = 7800 kg/m³, Ø50 mm between bearings, span L = 265 mm

FIND

- First bending natural frequency; margin over the 39,000 rpm maximum speed

ASSUMPTIONS

- Uniform simply supported beam (rigid supports); overhung impellers and the motor sleeve ignored, which makes this optimistic

EQUATIONS

ω₁ = (π / L)² √(E I / (ρ A)),   I = πd⁴/64,   A = πd²/4

SOLUTION

I = 3.068e-7 m⁴,  A = 1.963e-3 m²

ω₁ = (π / 0.265)² × √(197e9 × 3.068e-7 / (7800 × 1.963e-3)) = 8,829 rad/s

N₁ = 84,309 rpm → margin = 2.16 × 39,000 rpm

Result: First bending critical ≈ 84k rpm (needs > 1.2 × 39k = 47k rpm). Confirm with a rotordynamics/modal FEA including the impeller and magnet masses.

# C19  CFD post-processing calculations (stage-1 run, off-design)

FBD-5. Forces on a fluid particle in the rotating frame, the formulation CFX solves.

GIVEN

- Mass-averaged totals: P₀,in = 361.3 kPa, P₀,out = 668.7 kPa, T₀,in = 299.954 K, T₀,out = 322.93 K (R-134a)

- Per passage: ṁ = 0.385944 kg/s, blade torque 1.89043 N·m;  at r = 52 mm: Cθ = 95.2902 m/s, Cr = 45.3262 m/s

FIND

- Pressure ratio, efficiency, specific work three ways, slip factor and exit flow angle

ASSUMPTIONS

- Free vortex and continuity to move the r = 52 mm values to r₂ = 51.69 mm

EQUATIONS

PR = P₀,out/P₀,in;  Δh₀ = h(P₀,out, T₀,out) − h(P₀,in, T₀,in);  η = [h(P₀,out, s_in) − h_in] / Δh₀

Δh₀,torque = T ω / ṁ;   Δh₀,Euler = U₂ Cθ₂

σ = (Cθ₂ + Cr₂ tan β₂b) / U₂;   α₂ = atan(Cθ₂/Cr₂)

SOLUTION

PR = 668.7 / 361.3 = 1.851

Δh₀,T = 15.94 kJ/kg;  Δh₀s = 14.13 kJ/kg → η = 0.887

Δh₀,torque = 1.89043 × 3,141.6 / 0.385944 = 15.39 kJ/kg

Cθ₂ = 95.2902 × 52.0/51.69 = 95.87 m/s → Δh₀,Euler = 162.4 × 95.87 = 15.57 kJ/kg

σ = (95.87 + 45.60 × tan 40°) / 162.4 = 0.826;  α₂ = 64.6°

Stage power = 7 × 1.89043 × 3,141.6 = 41.6 kW at 2.70 kg/s

Result: PR = 1.851, η = 0.89; work: 15.9 / 15.4 / 15.6 kJ/kg (temperature / torque / Euler, within 3 %); σ = 0.83, α₂ = 64.6°

# Symbols

| Symbol | Meaning | Units |
| --- | --- | --- |
| ṁ | mass flow rate | kg/s |
| h, h₀ | static, total enthalpy | kJ/kg |
| s | entropy | kJ/kg·K |
| P, P₀ | static, total pressure | kPa |
| U | blade speed ωr | m/s |
| C, W | absolute, relative velocity | m/s |
| Cm, Cr, Cθ | meridional, radial, swirl (tangential) velocity | m/s |
| β, α | relative, absolute flow angle | deg |
| σ | slip factor | — |
| φ, ψ | flow and work coefficients | — |
| M | Mach number | — |
| ω, N | angular speed | rad/s, rpm |
| T | torque | N·m |
| σ_r, σ_θ | radial, hoop stress | MPa |
| Subscripts | 1 inlet/eye, 2 impeller exit, 3 diffuser exit, t tip, h hub, s isentropic |  |